## 說明
逐條合規對照表（附 EM-02-05 2026年5月版 氯餘量分析儀範例）
Compliance Schedule (clause-by-clause) — with EM-02-05 May 2026 worked example
填寫說明：黃色底色為填寫欄；灰色底色為示例行（正式呈交前請刪除）；「規格要求」欄為規格原文，不得改動。
依據：WSD EM-00-03（2025 年 10 月版）、EM-00-01（2023 年 12 月版）、EM-02-05（2026 年 5 月版）。港德環保科技編製，非水務署官方表格；特別規格及合約文件優先。編製日期 2026-09-03。
依據條款
• EM-00-03 Oct 2025 §1.1 (complete working unit; suitability as a system; hardcopy + softcopy)
• EM-00-03 Oct 2025 §1.2 Equipment Approval (submission contents, 1-month / 3-week cycle, true-copy certification, no ordering before approval)
• EM-00-03 Oct 2025 §2.3 Standards and Specification (equipment shall comply with the Specification; latest editions)
• EM-00-03 Oct 2025 §2.2 last paragraph (alternative offers accepted only on demonstrated equivalence)
• EM-00-03 Oct 2025 §2.1, §2.4, §2.5, §2.7, §2.8/2.9, §2.10, §3.4 (general rows applicable to every item)
• EM-02-05 May 2026 §1 General, §2 Design, §3 Accessories (worked-example rows)
填寫須知
• 每一行只放一項規格要求。「規格要求」欄必須一字不改引錄規格原文，不得改寫、撮寫或翻譯；如原文一句包含多項要求（例如 EM-02-05 §2 第二段同時要求 4-20 mA 輸出、可調上下限警報及設備故障警報），可拆成多行，但每行都要註明同一條款出處。
• 「所供數值」欄須填實際數值及單位，並與規格採用同一單位基準。例如 EM-02-05 的準確度以「量程百分比」（% of span）表示，若型錄以 ±mg/L 或「讀數百分比」表示，須換算後填寫，並在備註列明換算方法及型錄原文數值。
• 合規狀況只可選 Comply／Deviate／Not applicable 三者之一。選 Deviate 者，必須在備註說明偏差內容及理據，並交叉引用「標準對照表」的相關行；選 Not applicable 者必須寫明理由（例如特定規格未指定配套儀器），不可留空。
• 佐證欄要填到具體頁碼、圖則編號或報告編號，並在附件相應位置用方框或螢光筆標示數值，方便審批人員直接核對，減少來回補交。
• EM-02-05（2026年5月版）本身沒有細分條款編號，範例列的 B-01 至 B-21 只是模板自訂編號；正式呈交時須同時列出原文條款（§1／§2／§3 及段落／表格行），避免審批人員無法對應。
• Part A 為 EM-00-03 通用要求，適用於所有設備，每份對照表都應保留；Part B 換成該設備所屬的 WSD 標準規格；Part C 放特定規格（Particular Specification）及合約特定條款。三部分如有出入，以合約文件為準，並向工程師／項目經理查詢。
• 表頭須預留承建商蓋章及「certified true copy」核證位置。按 EM-00-03 §1.2，批准或有條件批准後三星期內須呈交一份已蓋章核證並納入所有修訂的文本；未獲批准前不得訂購製造。
• 除硬本外，須同時提交軟本（§1.1）。呈交限期（除非另有規定，合約開工後一個月內）及往返周期（三星期）請在表頭註明，方便自行追蹤。

## Header 表頭
表頭 Header
EM-00-03 §1.1 / §1.2
填寫說明：黃色底色為填寫欄；灰色底色為示例行（正式呈交前請刪除）；「規格要求」欄為規格原文，不得改動。
合約編號及名稱 Contract no. & title
僱主 / 工程師或項目經理 Employer / Engineer or PM
設備項目 Equipment item
品牌 / 型號 / 額定值 Make / Model / Rating (§1.2)
製造商及產地 Manufacturer & country of manufacture
適用規格 Governing specifications (EM-00-03 Oct 2025; equipment spec; PS clauses)
呈交編號 / 版次 / 日期 Submission ref. / rev. / date
呈交階段 Stage (First / Resubmission / Approved true copy)
編製 / 核對 Prepared by / Checked by
承建商蓋章及 certified true copy 核證位置 (§1.2)
附件清單 Attachments (technical details, literature, standard drawings; softcopy per §1.1)

## Part A EM-00-03
Part A — EM-00-03 通用要求（每份對照表保留）
General requirements applicable to every item
填寫說明：黃色底色為填寫欄；灰色底色為示例行（正式呈交前請刪除）；「規格要求」欄為規格原文，不得改動。
Row ID | 規格及條款 Specification & clause | 規格要求（原文）Requirement (verbatim) | 所供數值 / 設計 / 品牌型號 Offered | 合規狀況 Comply / Deviate / N.A. | 佐證參考 Evidence ref. | 備註 Remarks
A-01 | EM-00-03 §1.1 para 2 | "The Contractor / Contractor (hereinafter referred to as the Contractor) shall supply all items necessary for a complete working unit irrespective of whether all required components are separately detailed in the Specification." | Offered: scope of supply / bill of materials ref. | Comply | BoM ref. | list any loose items specified
A-02 | EM-00-03 §1.1 para 3 | "Particular attention is drawn to the necessity of equipment offered being suitable for the proposed installation and system as a whole, not as individual units, unless supply in loose items is specified." | Offered: system/interface description | Comply | GA drawing no. / schematic
A-03 | EM-00-03 §2.1 para 4 | "The limiting sound pressure level of the plant and equipment / Plant and Materials supplied under the Contract shall not exceed 90 dB(A) measured at any point 1m away from the equipment unless otherwise specified." | Offered: __ dB(A) at 1 m | Comply / N.A. | datasheet p.__ | if N.A. (e.g. no moving parts) state reason
A-04 | EM-00-03 §2.2 | "Asbestos material in any form shall not be used in any part of the plant and equipment / Plant and Materials supplied." | Offered: asbestos-free declaration | Comply | manufacturer declaration ref.
A-05 | EM-00-03 §2.2 | "Cadmium plated parts shall not be exposed to weather and high temperature at 50°C or above. Cadmium plated parts shall not be in contact with potable water." | Offered: plating / finish schedule | Comply | materials list ref. | cross-ref Materials-in-contact checklist
A-06 | EM-00-03 §2.3 para 1 | "Equipment offered shall comply with the requirements of the Specification, and shall be new, unused and manufactured to the highest commercial standards." | Offered: new & unused declaration | Comply | ¦
A-07 | EM-00-03 §2.3 para 2 | "The equipment shall be designed, manufactured and tested in accordance with the latest editions of the relevant International Standards and the standards referred to in the Specification." | Offered: list of standards & editions applied | Comply / Deviate | datasheet p.__ / Standards Comparison Table | if other standards used, complete Standards Comparison Table (§2.3 para 3)
A-08 | EM-00-03 §2.4 | "All plant and equipment / Plant and Materials shall be suitable for storage, installation and operation in a tropical climate with a maximum relative humidity of 100% and an average ambient temperature of 35°C over any 24 hour period and a maximum ambient temperature of 40 °C for 4 hours." | Offered: ambient rating __–__ °C, RH __% | Comply | datasheet p.__
A-09 | EM-00-03 §2.5 | "Unless otherwise specified, the manufacturer shall have at least three (3) years of experience in the manufacture of the equipment or similar items." | Offered: __ years | Comply | Manufacturer Qualifying Experience Statement
A-10 | EM-00-03 §2.7 para 2 | "All labels, nameplates, rating plates and notices shall be permanently marked in English unless otherwise specified. The proposed style, label material, inscription, location and means of fixing shall be submitted for approval before manufacture." | Offered: label schedule / drawing | Comply | label drawing no. | submit before manufacture
A-11 | EM-00-03 §2.8 para 1 & §2.9 table | "All equipment supplied shall have “Waterworks Finish” as per Clause 2.9 prior to despatch from the manufacturer's works." | Offered: coating system & BS 4800 colour ref. (e.g. Low Voltage Switchboard – Light Grey 18B21; stainless steel not coated per §2.8) | Comply / N.A. | paint spec ref.
A-12 | EM-00-03 §2.10 (1)–(5) & Table A | "No material or substance which, either alone or in combination with any other pipe or fitting, material or substance or with the contents of any pipe or fitting of which it forms a part, causes or is likely to cause pollution of fresh water shall be used in the construction, installation, maintenance, alteration, repair of any pipe or fitting which conveys or receives, or may convey or receive fresh water." | Offered: wetted materials schedule | Comply / N.A. | Materials-in-contact-with-fresh-water checklist | applicability depends on whether the part conveys/receives fresh water
A-13 | EM-00-03 §3.4 | "For electrical and instrumentation equipment, the packing containers shall be lined with waterproof paper and provided with a robust water vapour barrier, polyethylene sheeting of minimum thickness 0.5mm, to provide a desiccated package to BS 1133-19 for 6 months in tropical climate." | Offered: packing method | Comply | packing spec ref.

## Part B EM-02-05 範例
Part B — 範例：EM-02-05（2026 年 5 月版）餘氯分析儀
Worked example; replace with the equipment's own WSD Standard Specification. B-numbers are template numbering, not WSD clause numbers.
填寫說明：黃色底色為填寫欄；灰色底色為示例行（正式呈交前請刪除）；「規格要求」欄為規格原文，不得改動。
Row ID | 規格及條款 Specification & clause | 規格要求（原文）Requirement (verbatim) | 所供數值 / 設計 / 品牌型號 Offered | 合規狀況 Comply / Deviate / N.A. | 佐證參考 Evidence ref. | 備註 Remarks
B-01 | EM-02-05 §1 | "The chlorine residual analyzer shall be capable of continuously measuring either free or total chlorine residual in the sampled water." | Offered: free / total (state reagent set offered; state if convertible) | Comply | datasheet p.__ (measuring principle)
B-02 | EM-02-05 §1 | "All parts of the analyzer in contact with the sampled water shall be resistant to corrosion caused by chlorinated water and the chemical reagents used for measurement." | Offered: wetted-part materials list (e.g. measuring cell, tubing, valves, fittings) | Comply | wetted materials list / datasheet p.__ | cross-ref Materials-in-contact checklist for fresh-water parts
B-03 | EM-02-05 §2 para 1 | "The chlorine residual analyzer shall use colorimetric DPD chemistry (N,N-diethyl-p-phenylenediamine) to continuously measure either free or total residual chlorine, depending on the type of reagents installed in the instrument." | Offered: DPD colorimetric; reagent part nos. for free / total | Comply | datasheet p.__
B-04 | EM-02-05 §2 para 1 | "The analyzer shall be designed for low maintenance and capable of continuous, unattended operation for at least 30 days." | Offered: reagent autonomy __ days at __ min cycle; recommended maintenance interval __ days | Comply | datasheet p.__ (reagent consumption table) | show calculation basis
B-05 | EM-02-05 §2 para 2 | "A controller shall be provided in the analyzer to regulate the chlorination process." | Offered: built-in controller type (e.g. PID / on-off), control output type | Comply | manual p.__
B-06 | EM-02-05 §2 para 2 | "The analyzer shall include self-testing diagnostics and a front-panel LCD/LED display to show measurement readings and system status." | Offered: diagnostics list; display type & size | Comply | datasheet p.__
B-07 | EM-02-05 §2 para 2 | "One 4-20 mA analogue output signal for the measurement, one adjustable signal limit alarm ranging from 0% to 100% of the measuring range, and one equipment failure alarm shall be provided for remote monitoring and alarm annunciation." | Offered: qty of 4-20 mA outputs __; limit-alarm setting range __%–__% of range; failure alarm relay Y/N | Comply | datasheet p.__ / wiring diagram no. | may be split into three rows (output / limit alarm / failure alarm) citing the same paragraph
B-08 | EM-02-05 §2 para 2 | "Digital communication format such as Modbus or Profibus protocol etc. shall be provided subject to the market availability and application environment." | Offered: protocol(s) (e.g. Modbus RTU / Modbus TCP / Profibus DP / other) or statement of non-availability | Comply / Deviate | datasheet p.__ | if none offered, explain market availability / application environment
B-09 | EM-02-05 §2 table | "Measuring range : 0-10 mg/litre (free or total residual chlorine)" | Offered: __ – __ mg/L | Comply | datasheet p.__
B-10 | EM-02-05 §2 table | "Accuracy : better than ±5% of span from 0-5 mg/litre and ±10% of span from 5-10 mg/litre" | Offered: ±__% of span (0–5 mg/L); ±__% of span (5–10 mg/L) — convert from ±mg/L or % of reading and show conversion in Remarks | Comply | datasheet p.__
B-11 | EM-02-05 §2 table | "Lower limit of detection : 0.05 mg/litre" | Offered: __ mg/L | Comply | datasheet p.__
B-12 | EM-02-05 §2 table | "Cycle time : less than 3 minutes" | Offered: __ s / min | Comply | datasheet p.__
B-13 | EM-02-05 §2 table | "Operating temperature : 5-40°C" | Offered: ambient __ – __ °C (state sample-water temperature range separately if given) | Comply | datasheet p.__
B-14 | EM-02-05 §2 table | "Enclosure rating : IP65 with corrosion-resistant material" | Offered: IP __ (test standard); enclosure material | Comply | datasheet p.__ / IP test cert. no.
B-15 | EM-02-05 §2 table | "Analogue output signal : 4-20 mA, capable of driving a 500 ohm load" | Offered: max. loop load __ Ω | Comply | datasheet p.__
B-16 | EM-02-05 §2 table | "Alarm output contacts : Volt-free contact rated at 2A 220V a.c." | Offered: contact type & rating __ A @ __ V a.c.; volt-free confirmed | Comply | datasheet p.__
B-17 | EM-02-05 §2 table | "Supply voltage : 220V 50Hz a.c." | Offered: __ V __ Hz a.c., tolerance ±__% | Comply | datasheet p.__
B-18 | EM-02-05 §3 para 1 | "Where associated instruments such as sample water inlet strainer, water flow regulator valve, water gauge, chemical solution feeder and reservoir, etc. are specified in the Particular Specification, these instruments, together with the analyzer, shall be housed in a freestanding, floor mounted stainless steel panel." | Offered: panel type (freestanding, floor mounted), stainless steel grade, list of instruments housed | Comply / N.A. | panel GA drawing no. | N.A. only if the Particular Specification specifies no associated instruments — state PS clause
B-19 | EM-02-05 §3 para 2 (a) | "Unless otherwise specified in the Particular Specification, the following accessories and consumables, sufficient for continuous operation for one year, shall be provided with the analyzer :- (a) Chemicals" | Offered: reagent types & quantities for one year (calculation basis: cycle time × days) | Comply | consumables schedule ref.
B-20 | EM-02-05 §3 para 2 (b) | "(b) Installation kit" | Offered: kit contents | Comply | kit list ref.
B-21 | EM-02-05 §3 para 2 (c) | "(c) Maintenance kit" | Offered: kit contents | Comply | kit list ref.

## Part C 特別規格
Part C — 特別規格及合約特定條款
Particular Specification rows; quote PS clause verbatim; PS overrides Parts A/B where it says so
填寫說明：黃色底色為填寫欄；灰色底色為示例行（正式呈交前請刪除）；「規格要求」欄為規格原文，不得改動。
Row ID | 規格及條款 Specification & clause | 規格要求（原文）Requirement (verbatim) | 所供數值 / 設計 / 品牌型號 Offered | 合規狀況 Comply / Deviate / N.A. | 佐證參考 Evidence ref. | 備註 Remarks
C-01 | PS clause __ | （引錄特別規格原文）

## Summary 總結
總結及聲明 Summary & declaration
填寫說明：黃色底色為填寫欄；灰色底色為示例行（正式呈交前請刪除）；「規格要求」欄為規格原文，不得改動。
Comply 合規行數
Deviate 偏差行數
Not applicable 不適用行數
偏差清單（Row IDs）
承建商聲明及簽署 Contractor's declaration & signature
工程師 / 項目經理意見（留空）Engineer / PM comment